Job Hazard Analysis

| Task/Equipment: | Fluid Change for Control Compressor |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin and Bryana Borders |
| Date: | 4/16/19 |

Personal Protective Equipment Required:

Personal Protective Equipment Required:

Heavy Leather Gloves

Heavy Leather Gloves

Splash Goggles

Splash Goggles

Hard Hat

Hard Hat

Trainings Required*/Recommended:

Lock out tag out*

Equipment/Tools/Chemicals Required for the Job:

Compressor fluid, air filter, socket wrench, screw driver, filter wrenches, hand tools, funnel, oil/fluid absorbing compound

| Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Start standby compressor | No hazards present | N/A |
| - check to insure water flow to drain from water-cooled standby compressor or cooling fan is running for air cooled compressor | Finger cuts and water splash-back into eyes | Wear heavy leather gloves and splash goggles |
| - Push stop button on control pad to stop compressor being serviced | No hazards present | N/A |
| - Open main power disconnect at 3-phase distribution panel and secure using lock-out tag-out protocol | Skipping this step could cause severe burns to skin and eyes in step 6 | Follow lockout tag out protocol |
| - Isolate the compressor pneumatically and relieve system of air pressure until control panel pressure indicator reads zero | Skipping this step could cause severe burns to skin and eyes in step 6 | Control panel is there to show the current pressure. Wait until that hits zero before moving on to the next step. |
| - Remove fill tube cap | Skin burns, eye and facial injury | Close and secure pneumatic pressure isolation valve using lock-out protocol .Verify that all system pressure has been dissipated before opening system to service. Wear safety googles and heavy leather gloves |
| - Open drain valve and remove plug , Allow reservoir to drain completely | Skin burns | Wear heavy gloves |
| - Replace drain plug and close drain valve | No hazards present | N/A |
| - Fill fluid reservoir with fresh fluid to proper level | No hazards present | N/A |
| - Replace reservoir fill-cap and secure | No hazards present | N/A |
| - Reopen pneumatic isolation valve | No hazards present | N/A |

Additional Information:

Lab Coat

Lab Coat

Protection Suit

Protection Suit

Fall Protection Harness

Fall Protection Harness

High Vis Vest

High Vis Vest

Safety Shoes

Safety Shoes

Cryogenic Gloves

Cryogenic Gloves

Dust Mask

Dust Mask

Respirator

Respirator

Face Shield

Face Shield

Safety Glasses

Safety Glasses

Ear Protection

Ear Protection