Job Hazard Analysis

| Task/Equipment: | Readying Winter Boiler for Annual Inspection |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bryana Borders & Bill Partin |
| Date: | 4/12/19 |

Personal Protective Equipment Required:

Hard Hat

Heavy Leather Gloves

Rubber boots

Trainings Required*/Recommended:

Proper ladder use*, proper chain fall use*

Equipment/Tools/Chemicals Required for the Job:

Rotary Impact Tool

| Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Turn off boiler at panel | No hazards present | N/A |
| - Close and secure feed water globe valve and tag as closed | No hazards present | N/A |
| - Open main power disconnect and place lock-out device on handle | No hazards present | N/A |
| - Close main boiler gas cock and leave handle in the horizontal position | No hazards present | N/A |
| - Allow boiler to cool until pressure falls to 3 psi, then climb onto the boiler and open up steam drum vent | Ladder fall | Follow ladder safety protocol |
| - Close non-return and OY&Y stop valves on top of boiler | No hazards present | N/A |
| - Disable chemical feed pump if applicable | No hazards present | N/A |
| - Close surface blowdown stop valve closest to boiler and tag as closed | No hazards present | N/A |
| - Allow boiler to further cool until water temperature falls below 100 °F | No hazards present | N/A |
| - Open bottom blowdown valves and drain the boiler completely | No hazards present | N/A |
| - Remove manway covers and discard old gaskets | Finger pinch | Wear heavy leather gloves |
| - Remove all cross-tees and inspection plugs | No hazards present | N/A |
| - Rod out all water and steam piping associated with plus and tees, pressure and level safeties | No hazards present | N/A |
| - Remove water level safety float and place to the side | No hazards present | N/A |
| - Clean and remove any loose scale or debris in the mud drum | No hazards present | N/A |
| - Flush tubes wit power hose if needed | Wet floor can cause a slip and fall accident | Wear rubber boots |
| - Reclose bottom blowdown valves and attach a lock-out device over valves | No hazards present | N/A |
| - Open fire-side access door and visually inspect furnace refractory and tubes | No hazards present | N/A |
| - Contact city of Detroit boiler inspector for inspection appointment | No hazards present | N/A |

Additional Information:

Ear Protection

Protection Suit

Fall Protection Harness

High Vis Vest

Splash Goggles

Latex Gloves

Dust Mask

Respirator

Face Shield

Safety Glasses