Job Hazard Analysis

| Task/Equipment: | Removing Condenser Head From Chiller |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin & Bryana Borders |
| Date: | 4/11/18 |

Personal Protective Equipment Required:

Heavy Leather Gloves

Steel-Toe Boots

Safety Shoes

Hard Hat

Trainings Required*/Recommended:

Proper use of chain fall and hydraulic lift

Equipment/Tools/Chemicals Required for the Job:

Rotary impact tool, chain fall, hydraulic lift

| Tasks/Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Attach chain fall or hydraulic lift to lift hook at top of head | Injury from swinging lift hook | Hold the lift hook while transporting or lowering |
| - Remove bolts from perimeter of head | Wrist twist | Careful use of impact tool, wear heavy gloves |
| - Raise lifting device to support head | Head could fall on someone’s foot if the hook isn’t secured correctly | Double check to make sure the hook is secured on the condenser head. |
| - Position one person to guide head away from condenser while the other operates the lift device | Heavy swinging object could hit someone | Be careful when operating the lift. Proper training required |
| - When head is clear of condenser, lower to floor and lay flat | Foot injury due to heavy steel head falling | Wear steel-toe boots |
| - Manually move head to a safe storage location | Heavy swinging object could hit someone | Be careful while operating a lift. Proper training required |
| - Remove O-ring and wipe clean with a cloth ,store in a clean place for reuse | No hazards associated with this step | N/A |
| - Scrape and clean loose scale from head surfaces | Tolls used to scrape head surfaces could puncture the skin | Use heavy duty gloves while cleaning the head surface |
| - Inspect condenser tubes for scale or corrosion | No hazards Present | N/A |

Additional Information:

- This task must be done with 2 people

Lab Coat

Protection Suit

Fall Protection Harness

High Vis Vest

Splash Goggles

Dust Mask

Respirator

Face Shield

Safety Glasses

Ear Protection