Job Hazard Analysis

| Task/Equipment: | Descaling Tower Nozzles |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin & Bryana Borders |
| Date: | 4/12/19 |

Personal Protective Equipment Required:

Rubber Boots

Hard Hat

Light Leather Gloves

Trainings Required*/Recommended:

Ladder safety*, confined spaces training*, lock out tag out training*

Equipment/Tools/Chemicals Required for the Job:

Hand tools, screw driver, chipping tool

| Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Turn off tower controls at main control center MCC panel using lock out tag out protocol | If tower controls are not turned off and locked out/tagged out it could cause serious injury in steps 4-7 | Second person must verify correct disconnects are locked out and tagged out |
| - Open main power disconnects at tower and secure using lock out protocol | If power is not disconnected and locked out/tagged out, it may result in serious injury in steps 4-7 | Second person must verify correct disconnects are locked out and tagged out |
| - Climb tower ladder, open entrance doors and enter tower confined space | Fall from ladder | Ladder Safety Training |
| - Remove upper horizontal tower fill to expose nozzles | Decapitation, severe head trauma due to fans starting unexpectedly | Lock out and tag out fan power disconnect, post second person to be sure no one enables tower fans , use confined spaces protocol |
| - Start condenser pumps to provide water flow | Decapitation, severe head trauma due to fans starting unexpectedly | Lock out and tag out fan power disconnect, post second person to be sure no one enables tower fans |
| - Use chipping tool to loosen and free scale from nozzles | Decapitation, severe head trauma due to fans starting unexpectedly; cuts from chipping tool | Lock out and tag out fan power disconnect, post second person to be sure no one enables tower fans; Use leather gloves to prevent cuts |
| - Replace upper fill | Decapitation, severe head trauma due to fans starting unexpectedly | Lock out and tag out fan power disconnect, post second person to be sure no one enables tower fans , use confined spaces protocol |
| - Exit confined space and close access doors and secure | Fall from ladder | Ladder Safety Training |

Additional Information:

- Two-person Task

Lab Coat

Protection Suit

Fall Protection Harness

High Vis Vest

Splash Goggles

Dust Mask

Respirator

Hard Hat

Face Shield

Safety Glasses

Ear Protection