Job Hazard Analysis

Personal Protective Equipment Required:

| Task/Equipment: | Lubricating Tower Fan Bearing and Tensioning Fan Power Bands |
| --- | --- |
| Department: | Powerhouse |
| Analyzed By: | Bill Partin & Bryana Borders |
| Date: | 4/12/19 |

Hard Hat

Light Leather Gloves

Trainings Required*/Recommended:

Ladder Safety Training, Lock out tag out protocol*

Equipment/Tools/Chemicals Required for the Job:

Screw driver, tensioning wrench and grease gun

| Steps | Hazards Present | Safety Measures and Controls |
| --- | --- | --- |
| - Open disconnect at main control center MCC panel using lock-out tag-out protocol | Turning off wrong disconnect could cause serious injury in step 4 | Second person must verify that correct disconnect was opened and locked out |
| - Open main power disconnect mounted on tower structure and secure using lock-out tag-out protocol | Forgetting to open disconnect could cause serious injury in step 4 | Second person must verify that correct disconnect was opened and locked out |
| - Climb tower ladder and open access doors to fan compartment | Ladder fall | Ladder safety training |
| - Use tensioning wrench to adjust power band to desire tension | Hand loss or injury due to fans starting unexpectedly | Lock out and tag out fan power disconnects and post second person to insure that no one enables fans |
| - Attach grease gun hose to grease fittings and pump in grease | Ladder fall | Ladder safety training |
| - Close access door and secure | Ladder fall | Ladder safety training |

Additional Information:

-

Lab Coat

Protection Suit

Fall Protection Harness

High Vis Vest

Safety Shoes

Splash Goggles

Cryogenic Gloves

Latex Gloves

Dust Mask

Respirator

Hard Hat

Face Shield

Safety Glasses

Ear Protection